# Earthquakes Damage Mitigation Guidelines

ESD Target
Guideline Objectives
Main Issues Addressed
Issues Excluded
Background
Definitions
Underlying Assumptions
Aspect Identification
Assessment of Vulnerability
Mitigation Methodology
Mitigation Techniques
Environmental Targets
Compliance
Policy
References

ESD Target

Every building under State Government responsibility shall be designed and managed with the expectation that, sometime during the life of the structure, it will be the subject of an earthquake event.

Guideline Objectives

- identify design criteria and provide recommendations for earthquake resistance, for all specific building types and all building services

- identify the affects that soils and location have on earthquake design loads

- identify the consequences of design and detailing inadequacies in building vulnerability

- identify building structural and architectural details and requirements for earthquake resistance

- identify the potential failure mechanisms with regard to the various and alternative building services and framing systems available

- provide an awareness for planners, designers and managers of the potential hazards caused by earthquakes and the solutions available to reduce the vulnerability of buildings, structures or services should an earthquake occur.

Main Issues Addressed

— the nature of potential damage to buildings and services within the government's building porfolio 

—the relationship between the Strategic Asset Management process and:

- Soil and Foundation Conditions

- Building Classification/Use

- Structural Systems

- Mechanical Services

- Electrical Services

- Hydraulic Services

- Architectural Features

- Access and Egress

Issues Excluded

— Compliance with the relevant codes and regulations 

— Development of post-disaster strategies 

— The methodology to overcome deficiencies in design for existing buildings 

— Specific details to cater for earthquakes to avoid possible damage 

— Buildings for which the Queensland State Government has no responsibility 

— Infrastructure such as roads, dams, masts, aerials, bridges, etc. 

— The methodology does not include provision for emergency services

Background - Earthquakes and how they arise

Earthquakes are caused by the differential movement of the tectonic plates which form the earth's crust. The differential movement of the plates, both at the plate's boundaries and within a plate, generates uneven stresses within the subsurface rock. When the stress becomes too great for the rock matrix to resist, rapid shearing and deformation takes place releasing the stored energy.

The energy released leads to a series of compression waves that pass through the crustal strata at varying speeds and magnitude depending on the properties of the strata encountered.

The waves are a complex mix of horizontal and vertical oscillations known as P, S and L waves. It is the S waves that generally cause damage to buildings, services and other infrastructure. The waves cause the ground to move in both horizontal and vertical directions (in extreme conditions by the order of many metres).

A stylized Seismograph Output

The soil type and profile on which any building sits influences the size of ground motion encountered. By example, the ground motion through a soft, silty sand is generally more damaging than the ground motion from the same earthquake intensity through a dense, gravelly soil.

Damage can also be associated with the presence of faults in rock formations, lineaments and at the interface of other geological features. Large lateral movements are often observed along pre-existing faults as the compression waves pass through the fault.

Australia is located within the central section of the Australian tectonic plate. Hence all of the seismic activity of any significance experienced within Australia has been derived from 'intraplate' earthquakes. These quakes are limited to the top 50 kilometres of the crust, are random in their location, and are generally smaller in magnitude than those associated with quakes arising at plate boundaries.

The hazard rating for an area is determined from past events, whether by electronic data monitoring or from peoples' recollections.

Queensland's hazard areas are generally confined to the land and continental shelf to the east of the Great Dividing Range.

The Maryborough - Gladstone region is considered an area of medium hazard rating, with the remainder of the coastal strip being medium to low. Western Queensland is generally considered to have a low hazard rating, although this is partly a result of the lack of data for the area.

Definitions

Relative Risk Factor

The "Relative Risk Factor" has been developed for this guideline to assist planners and designers in the selection of the most suitable site for a building. The factor is subjective and dependant on the type or component of the building or structure being assessed.

Damage

Four levels of damage to buildings were defined after the Newcastle earthquake. Damage notices using the different levels were placed on buildings and colour coded accordingly.

Damage can be defined as either minor or major, with sub-definitions of each.

Minor

TYPE A
Little or no damage, building is satisfactory for continued habitation (hairline cracks may be visible). 
TYPE B
Some damage. Building is satisfactory for continued habitation but repairs are required

Major

TYPE C
Sufficient damage to building to be hazardous to occupants although building is repairable. 
TYPE D
Building is hazardous to public and cannot be repair to original condition. Building is to be demolished.

Gravitational Acceleration (g)

Acceleration due to gravity; taken as 9.81 m/s2.

Irregular Structure/Building

A building that in plan or elevation varies in width from one section of the building to another by more than 15%. Typically this would be an "L" or "U" shaped building or large area podium floor plan with a slender tower over.

Soft Storeys

A section of a building that varies in stiffness by more than 30% to the floor above or below. These are typically open areas, under-cover carparks, or with a large open foyer or vestibule, with a rigid framed building above.

Soil types

The following soil profiles are defined in AS1170 Part 4 - 1993 and are used to determine forces on the foundations of structures. Each of the soil types has been given a type letter to enable easier use within these guidelines.

General structures:

Type A - Low strength rock or better
Type B1 - Extremely low strength rock or better
Type B2 - Not more than 30m of medium dense coarse sand and gravel, firm or stiff clays or controlled fill
Type C - More than 30m of medium dense coarse sand and gravel, firm or stiff clays or controlled fill
Type D - A soil profile of 20m or more with 6m to 12m of very soft to soft clays, very loose to loose sands, silt and/or uncontrolled fill
Type E - More than 12m of very soft to soft clay, very loose to loose sands, silt and/or uncontrolled fill

Domestic Structures:

Normal - Other than Soft
Soft - Any soil profile with more than 5m of soft clay, loose sand, silt and/or uncontrolled fill.

Underlying Assumptions

The ground motions specified in AS1170 Part 4 - 1993 are for the 'design earthquake' based on an estimated 90% probability of these ground motions not being exceeded in a 50-year period.

Aspect Identification

Typical building elements that are damaged during earthquakes:

- internal fittings and furniture movement;

- tall cupboards falling over;

- light fittings, air conditioning and ceiling units dislodging and coming loose;

- objects in high cupboards falling out causing damage and potential injury;

- wall linings which do not have capacity for horizontal or vertical movements;

- water damage due to broken pipes;

- loss of power due to broken power cables;

- brick walls with insufficient strength cracking and collapsing;

- unsupported masonry parapets falling over due to insufficient anchorage or bracing;

- windows cracking due to building movement;

- loss of communications network;

- precast panels and other architectural features falling from the building facades having insufficient or ineffective fixings;

- tiltup wall panels losing support due to insufficient or ineffective fixings;

- water pipes breaking at expansion joints and equipment connection points;

- water storage tanks (especially those on roofs) rupturing and or moving and breaking pipework;

- mechanical equipment moving off bases and causing disconnection;

- electrical equipment moving off bases and causing disconnection;

- power backup battery facilities falling off shelves causing loss of backup power;

- loss of support to suspended slabs from masonry walls where reinforcement has not continued through to the slab, particularly vulnerable in unreinforced masonry buildings;

- rotation of retaining walls due to increased vertical and horizontal earth pressures;

- differential movement between foundations and floor slabs due to ground movements;

- insufficient support to air conditioning equipment;

- differential movement between various soil types supporting foundations;

- irregular shaped buildings have different modes of vibration for the different sections of the building causing concentration of stresses and excessive loads at discontinuities;

- "Soft storeys" failure due to lack of support to withstand horizontal loading;

- load bearing walls with no continuity to upper or lower floor framing systems;

- failure of vibration isolation support;

- inadequate foundation system for earthquake loads;

- suspended slabs on unreinforced masonry walls losing support due to the lateral displacement of the wall under;

- columns cracking;

- punching of columns through suspended slabs;

- broken pipework;

- loss of service functions.

Assessment of Vulnerability

One method for rapidly assessing the potential vulnerability of buildings is through the use of relative risk factors. By assigning a numeric value to key, influential criteria governing the magnitude of any quake disaster, it is possible to target finite resources in a systematic and logical fashion.

Three elements are critical to any calculation of relative risk:

- the increased design load requirement (by the earthquake);

- the level of functionality for post-disaster performance;

- the number of occupants generally using the building.

Relative risk factors can be assigned using the following matrix:

| Relative Risk Factor | Soil Profile Risk | Ground Acceleration | Post-disaster Function | No. of Occupants |
| --- | --- | --- | --- | --- |
| 1 | Type A | 0.3 - 0.4 | Residential (singles) | < 5 |
| 2 | Type B | 0.4 - 0.6 | Residential (family) | 5 to 10 |
| 3 | Type C | 0.6 - 0.8 | Non Essential eg. Commercial | 11 to 20 |
| 4 | Type D | 0.8 - 1.0 | Desirable eg. Assemble Hall | 21 to 50 |
| 5 | Type E | > 1.0 | Essential eg. Hospital | > 50 |

By assigning the relative risk values and summing the totals for each building it becomes clear where available resources can be assigned.

| Building | X | Y | Z |
| --- | --- | --- | --- |
| Locality | 4 | 2 | 1 |
| Soil Profile | 1 | 5 | 4 |
| Post-disaster Function | 3 | 5 | 1 |
| No. of occupants | 2 | 3 | 1 |
| Total | 10 | 15 | 7 |

Vulnerability could also include the ability of services to function following a quake. Accordingly an additional classification could be added which reflects the number of essential services located within a building, eg. backup power, emergency water storage, fire systems, sewerage control, communications equipment and computer systems. For example. Relative risk factors for the number of essential services (or any other factor pertinent to the time) could be assigned as follows:

| No. of Services | Relative Risk Factor |
| --- | --- |
| 1 | 1 |
| 3 | 2 |
| 6 | 3 |
| 9 | 4 |

Mitigation Methodology

Assessment of Existing Buildings

A determination of which elements of an existing building will be susceptible to earthquake damage must be made. Where necessary a management plan can be developed for the building such that its use and/or its structural components can be modified so as to minimise potential injury or loss of life.

A management plan would include the recording of the framing system, facade system and also whether the building contains any vulnerable elements, such as unreinforced masonry, soft storeys, irregular structure shapes and any mechanical and electrical systems that may be required for post-disaster functionality of the building.

Flow chart to aid assessment of an existing building.

Planning and Design of New Buildings

Numerous elements have to be considered during both the planning and design of a new building. Those involved in the planning phase must take a broad perspective, taking note of how the building will relate in form and function to the wider socio-administrative environment. By example, one element to consider would be how the build would be used post-disaster.

Flow chart to aid in planning for a new building.

Design involves the selection of the appropriate facade systems, structural framing and foundation system, anchorage of mechanical and electrical components, provision for sufficient flexure in service pipes and ducts, and restraint of large moveable items.

Also, design should provide both the occupants with the ability to exit the building quickly in an emergency, as well as the opportunity for emergency service personnel to enter the building post-disaster.

All buildings will "move" to some extent during an earthquake. Some structures may suffer a permanent "set," leading to problems such as jammed doors and windows, cracked walls or differential settlement of foundations.

Buildings designed to AS1170 Part 4 - 1993 should provide good to adequate performance during and after an earthquake.

Flow chart to aid in the design of a new building.

Management of Existing Buildings

Building Management, Operational and Emergency Plans should be regularly reviewed and updated to anticipate issues arising from an earthquake event.

Priority should be given to strategies for minimising loss of life and injury. Clear and concise evacuation plans and strategies will assist in bringing order to what will be a chaotic environment.

An inventory of equipment useful in the post-disaster phase should be included in the building's management plan. The roll-out of Emergency Schedules and Procedures for checking the structure for weakened or damaged components will also be a post-disaster priority.

The management plan would include at least the following:

- Building Description

- Use of Building

- Building Elements

- Service Equipment

- Occupant Register.

Flow chart to aid creation of suitable management plans.

Maintenance of Existing Buildings

The building's existing maintenance plan should be reviewed so as to incorporate systematic checks on fabric integrity. Where possible these checks should include the inspection of elements like:

- brick ties to ensure they are not damaged or broken due to rust, etc;

- anchor bolts to service equipment have not corroded, loosened or missing;

- watering systems or landscaping have not caused a change in the water table or moisture content of the soil, etc.

These checks, tailored to the individual building, should ensure that the structure continues to function in accordance with its original design specification. The maintenance regime must remain a logical supplement to the building's overall management strategy.

The development of these procedures must be flexible and fluid. The maintenance process should include the continual upgrade of the following procedures:

- Building Description

- Occupancy Register

- Equipment Register

Flow chart for the maintenance of existing buildings.

Post Disaster and Disposal

After an earthquake, a rapid inspection of all buildings must be carried out. The inspection should classify each structure as being either "safe" "for occupancy" or "for operation", "is unsafe and requires repair " or is "unsafe and building requires demolition". Such assessment must be carried out by experienced building inspectors or structural engineers.

Contingency plans must ensure that all persons who occupied the building during the event have been accounted for. Emergency service personnel may require immediate access to retrieve injured persons; the need to co-ordinate such search exercises must be included in the plan. If the building has not been provided with post-earthquake safe operation, emergency service personnel may also be at risk while retrieving those injured.

As a consequence of an earthquake, the assessment of the building will include the requirements of emergency services for the:

- safe passage of rescuers;

- stability of the structure;

- rescue of trapped persons;

- access for emergency services (both personnel and vehicles);

- egress for occupants.

Emergency Services organisations should be contacted to assist in the development of disaster strategies and plans for individual buildings.

Flow diagram for post earthquake procedures.

Mitigation Techniques

Damage mitigation techniques must be deployed throughout the lifetime of a building. Within the Strategic Asset Management cycle this means consider damage mitigation practices at each stage of the cycle. Responsibility for ensuring the necessary consideration is given to damage mitigation lies predominantly with planners, designers and asset managers.

The following matrix provides a brief outline of the kinds of damage mitigation issues that may arise during the Strategic Asset Management cycle.

By example, for those at the 'design' stage who are considering 'electrical' aspects of a building - click the box containing "2.5"

|  | Planning | Design | Asset Mgment | Maintenance | Post- Disaster | Risk |
| --- | --- | --- | --- | --- | --- | --- |
| Soil Conditions | 1.1 | 2.1 | 3.1 | NA | 5.1 | 6.1 |
| Building Classification | 1.2 | 2.2 | 3.2 | NA | 5.2 | 6.2 |
| Structural | 1.3 | 2.3 | 3.3 | 4.3 | 5.3 | 6.3 |
| Mechanical | 1.4 | 2.4 | 3.4 | 4.4 | 5.4 | 6.4 |
| Electrical | 1.5 | 2.5 | 3.5 | 4.5 | 5.5 | 6.5 |
| Architectural | 1.6 | 2.6 | 3.6 | 4.6 | 5.6 | 6.6 |
| Hydraulic | 1.7 | 2.7 | 3.7 | 4.7 | 5.7 | 6.7 |
| External to site | 1.8 | 2.8 | 3.8 | NA | 5.8 | 6.8 |
| Emergency Services | 1.9 | 2.9 | 3.9 | 4.9 | 5.9 | 6.9 |

Environmental Targets

Australian earthquake loading standards for specific building types have been in force since 1993.

The Foreword to the Australian Standard AS1170 Part 4 - 1993, Earthquake Loads states:

"The purpose of designing structures for earthquake loads is to -

(a) minimize the risk of loss of life from structure collapse or damage in the event of an earthquake:

(b) improve the expected performance of structures; and

(c) improve the capability of structures that are essential to post-earthquake recovery to function during and after an earthquake, and to minimize the risk of damage to hazardous facilities."

The design of structures to this target will not necessarily prevent structural and non-structural damage in the event of an earthquake. The provisions provide the minimum criteria considered to be prudent for the protection of life by minimizing the likelihood of structural collapse.

Buildings constructed prior to the code should be reviewed and a risk assessment documented, particularly where buildings are designed for large occupancy, institutional or post-disaster uses. Retro-fitting usually has a high financial and resource cost; a cost benefit analysis to determine the level of retrofit must be documented.

Compliance

All buildings and structures are required to be designed in accordance with the following Australian Standards and the relevant standards pertinent to the building components being designed or constructed.

The following codes are both minimum and applicable to design for earthquakes in Australia to attain the potential for minimisation of failure due to earthquakes.

- AS 1170.1 Part 1 (1989) SAA Loading Code - Dead and live loads and load combinations

- AS 1170.4 Part 4 (1993) Earthquake Loads

- Building Code of Australia

Post quake, Standard AS 2601 (1991) The demolition of structures, is pertinent.

Policy

These Guidelines are to be used in the planning, design, management, operation and maintenance stages of a new building, and also in the management and maintenance of existing buildings.

This guideline provides only a background to the requirements necessary for the planning, design management, operation and maintenance of any building or structure. Before undertaking and specific structural or administrative change seek advice from relevant professionals with appropriate expertise and experience in earthquake engineering planning, design, emergency operation and management.

References

Applied Technology Council, 1989. 
Procedures for the Post Earthquake Safety Evaluation of Buildings
Applied Technology Council ATC-20,California.
A variety of studies and photographs which indicate typical damage areas and indicates where damage can occur and where to look for it in areas which failure is not always visible from the outside
ESC, 1993.

The Practice of earthquake hazard assessment. 
International Association of Seismology and Physics of the Earths Interior and European Seismological Commission.
An outline of the different methods used by the various countries in the earthquake hazard assessment for their areas
Federal Emergency Management Agency, 1996.

Guidelines for the Seismic Rehabilitation of Buildings. 
Federal Emergency Management Agency (Report No. FEMA 273), Washington DC.
Guidelines outlining methods of repairing buildings after an event. Includes determination of loads, soil condition criteria, hazard levels, framing systems and models and analysis of various building systems
Federal Emergency Management Agency, 1988.

Rapid Visual Screening of Buildings for Potential Seismic Hazards: Supporting Documentation. 
Federal Emergency Management Agency (Report No. FEMA 155), Washington DC.
Contains sketches and photographs which identify the various building types and framing systems as well as identifying potential hazard components of a building and the failure mechanisms
Federal Emergency Management Agency, 1989.

Seismic Evaluation of Existing Buildings: Supporting Documentation.
Federal Emergency Management Agency (Report No. FEMA 175), Washington DC
Contains typical forms used for evaluating seismic resistance of buildings including the responses
Federal Emergency Management Agency, 1988.

Rapid Visual Screening of Buildings for Potential Seismic Hazards: A Handbook. 
Federal Emergency Management Agency , ATC-21, Washington DC.
Outlines a number of procedures for rapid visual screening of buildings for potential hazard and has developed a series of Q & A checklists to assist
Hughes P.R., Rynn J.M.W., 1993.

Limitations Of The Cornell-Mcguire Earthquake Risk Method: An Engineering Viewpoint For Australia. 
National Earthquake Conference, Central United States Earthquake Consortium.
A discussion on the limitations of the typical method of determining earthquake risk as used by other countries for Australia
IEAust, 1990.

Newcastle Earthquake Study. 
The Institution of Engineers Australia.
Document prepared by the Institution of Engineers discussing issues such as construction, design, insurance, previous seismicity, safety assessment, post disaster functions, risk management and heritage issues that were raised due to the Newcastle Earthquake
Newcastle City Council, 1989. 
Newcastle Earthquake Response Record. 
Newcastle City Council, Newcastle.
Reports by the various emergency departments into the procedures undertaken after the event and the problems that occurred
NCC and CERA, 1991.

Proceedings Papers "What We Have Learnt From the Newcastle Earthquake" Lessons in Building Design, Regulation Disaster Management, Earth Science and the Legal and Insurance Implications. 
The University of Queensland, Australia.
A series of papers and notes on the Newcastle Earthquake ranging from design issues, emergency procedures, insurance aspects, construction issues, latent defects
Pedersen I.S., Hughes P.R., 1993

Engineering Implications for Continental Earthquakes: Inferences from the 1989 Newcastle Earthquake. 
National Earthquake Conference, Central United States Earthquake Consortium
Paper discussion on the geology, history of the area, seismicity, extent of damage and design requirement in the Newcastle area after the Newcastle Earthquake
Rynn J.M.W., Hughes P.R., Brennan E., Pedersen I.S., Stuart H.J., 1993.

Final Report Of Urbanised Areas Of Australia Phase 2 1992-1993 Program "Earthquake Zonation For Southeast Queensland". 
Centre for Earthquake Research in Australia.
Report which outlines the development of the earthquake zonation in Australia, in particular South East Queensland
Rynn J.M.W., 1993.

Methodology for Earthquake Zonation of Continental Regions-Example for the Sydney Region, Australia. 
National Earthquake Conference, Central United States Earthquake Consortium.
Paper discussion on the method of determining the earthquake zones in Australia, in particular Sydney
Swiss Reinsurance, 1990.

Newcastle: The Writing on the Wall. 
Swiss Reinsurance Company, Zurich Switzerland.
Reinsurance report on damage caused by the Newcastle earthquake.

The assistance of Hughes Consulting Services Pty Ltd, Indooroopilly, Brisbane is acknowledged

Gift Policy | Copyright | Disclaimer | Privacy | Access keys | Last updated: 30 June, 2008

© The State of Queensland (Department of Public Works) 2003.

Queensland Government Gateway

Mitigation Techniques

Soil Conditions

Other than the selection of the foundation system - piles, bored piers, pad footings, strip footings or raft - the design of a building is significantly affected by the soil profile that exists at the site. Load coefficients are determined by the type of soil and the depth of the soil profile.

Each of the five soil types listed for 'general structures' will impose different design loads on a building and therefore the type of structure required. Similarly, the two classifications for 'domestic structures' provide basic coefficients for domestic design. These are defined in AS1170 Part 4.

Building Classification

The classification and purpose of the building provides one of the design factors for determining the earthquake loads. Those buildings which form post-disaster functions such as hospitals and assembly buildings (which can house displaced persons), attract higher design load factors than those that do not.

Structural

When considering a structural framing system to meet earthquake requirements, a number of issues must be addressed. These include:

- elimination of soft storeys;

- elimination of irregular or partially irregular shaped buildings;

- detail requirements for masonry elements;

- location of stiffening elements, eg. bracing walls, stair wells, lift shafts, symmetrically throughout the building, etc;

- continuity of load bearing members;

- selection of the appropriate foundation system; and

- determination of earth pressure on retaining walls

There are also five levels of design and detailing required by AS1170 Part 4, varying from simple static analysis and unreinforced masonry, to dynamic analysis and elimination of all masonry elements, towards completely reinforced masonry with specific detailing requirements for general buildings. For domestic structures, there are three levels of design and detail requirements. Typical structural elements that must be considered are:

- unreinforced load bearing walls;

- reinforced load bearing walls;

- braced frame (timber - concrete - steel);

- moment resisting frame (concrete - steel - timber);

- retaining walls.

Selection of the appropriate foundation and framing system and attention to detailing requirements for masonry and framing are particularly important in minimisation of potential earthquake damage.

Mechanical

Mechanical services are usually limited to major buildings such as assembly halls, hospitals, institutional, commercial and industrial buildings. The importance of these components is not only dependant upon their post-disaster function, but also on the possible effect on other components in the building, such as pipework and electrical installations.

Consideration of the consequences of failure during planning and procurement, management and maintenance is critical to the post-disaster availability and functionality of the building.

Typical mechanical items in major buildings include:

- generators;

- water tanks;

- cooling systems;

- boilers;

- pipework;

- air conditioning units and associated duct work;

- pumps;

- switchboards and I.T. systems.

Many of these items are fixed to the structure with vibration isolators for in-service operations, which in many cases are inadequate to resist earthquake loads. Also, pipework is often rigidly fixed to the adjacent support structure with no allowance for lateral movement between mechanical equipment and the structure.

Electrical

Electrical services are provided generally to all buildings, albeit in varying capacities. The importance of continued operations after an earthquake is dependant upon the post-disaster requirements for the building.

It is highly probable that mains power will be unavailable immediately after a quake. Therefore the provision and successful operation of backup power will be critical to the continued functionality of the building post quake.

Power generators will be in short supply after a quake. The advanced provision and subsequent successful operation of a backup electrical supply is crucial.

Architectural

During earthquakes, loads are applied in horizontal and vertical directions. Items that fail under these conditions are items that generally rely on gravity to remain in place. Ceiling tiles, light fittings and objects suspended from ceilings or roofs generally have little or no vertical or lateral support (especially for reversal of loads) or are inadequate to provide restraint during an earthquake. These objects can fall through opened grid systems and severely injure occupants below.

The building shape and framing system is critical to the successful resistance to an earthquake. Soft storeys should be avoided, eg. open undercover car parks within rigid framed buildings. Lift and stair shafts should be located symmetrically throughout the building. Otherwise the building will be subjected to torsional forces during an earthquake. Similarly heavy objects such as water storage tanks should be located within the centre of the building and as low as possible within the height of the building. Heavy objects should be situated at ground level, where swaying from the imposition of earthquake loads is reduced.

Hydraulic

Water supply and sewerage systems are often damaged during an earthquake. Water pipes may rupture or shear depending on the severity of the earthquake and similar damage may occur to sewerage systems in the ground, rendering both services inoperable.

These services are generally located underground and external to the building. Rectification in the short term immediately after an earthquake is usually difficult to achieve due to access problems. Provision of these services after an earthquake would generally be of a temporary nature until full services can be provided (which could take many months to reinstate).

External Site Considerations

Consideration of external services is particularly important for buildings which have a post-disaster function - such as a hospital. A quake, depending on its severity, can shear off pipework for water, sewerage, gas and electricity. Fault lines or differential settlement (slumps and slides) of embankments after an earthquake may hinder emergency vehicle access.

During the planning stages of a building, planners should consider matters like:

- If disaster occurs, can the road network provide access to the specific building, especially ones with a post-disaster function;

- Can existing services such as water supply, sewerage, communications, power, cope with an earthquake load and continue to provide the services to the level for which they were designed.

Emergency Services

Facilities such as hospitals, temporary accommodation for the displaced population and communications structures are critical to the subsequent success of Emergency Services activities.

Reliance on mobile telephones after an earthquake for emergency communications should not be made. If power is removed from the communications tower, or if the tower collapses, then service in the area is lost. Alternative methods of communication must be established.

Planning

Planning for the design of all new buildings should incorporate a complete geotechnical investigation of the site to determine the effect of the soil profile on any earthquake imposed load. This will then allow a comparative assessment of alternative sites to be carried out. It will also highlight whether a building is located in a potentially high vulnerability area for earthquakes. The site investigation will also provide information to determine the type of construction required for the building and also the level of design required. It will also indicate to the building services engineers the standard of connections for services equipment required.

Refer also to:

- Design of New Buildings

- Assessment of Existing Buildings

- Assessment of Vulnerability

1.1 Soil

Most soil investigations for small projects may only go to a depth of 2 to 3 metres. In most domestic building cases this is sufficient as local geological conditions (where applicable) can be determined through advice from local agencies.

For major building infrastructure projects such as hospitals, schools, commercial, institutional and industrial buildings, where the building can be used for post-disaster functions, soil profiles should extend to a depth of approximately 30 metres unless low or better strength rock is encountered. Care should be taken that the rock encountered is not a large boulder or minor seam.

The strength and depth of the soil has a bearing on the load factors, just as the locality of the site has a bearing on the load factors. These two load factors can significantly increase the strength requirements of the structure which will also affect project costs. In order to minimise both costs (construction and life cycle maintenance) and vulnerability, the building should ideally be located in a low risk area and on a rock foundation.

Possible future modifications should also be considered to ensure that the soil and foundation conditions do not change over the life of the building. For example, an increase in water table levels in sandy areas will increase the risk of liquefaction and/or reduce the bearing capacity of the soil. In turn, this may increase the building's vulnerability and reduce its life cycle availability.

1.2 Building Classification

The combination of the use and classification of the building, in conjunction with the soil conditions, must be considered during the planning process for the building's location. These factors have cumulative load implications for the design of the structure, particularly as building components and building services can add to the cost of meeting the overall cumulative load. So, for buildings with a critical post-disaster function, the preference should be to locate the structure in an area that minimises vulnerability. This may be achieved for example, by locating the building on a site that has a soil profile comprising of dense gravelly material rather than loose sand or deep alluvial deposits.

1.3 Structural

In planning for the building's framing system, the type of minimum design and detailing required is controlled by the locality, the soil conditions, and the intended use of the building. Reference should be made to Table 2.6 of AS1170 Part 4 which defines the design required for the soil conditions and the type of building.

Selection of an appropriate locality and site with soil profile that minimises design loads provides significant savings to cost of the structure and framing requirements.

1.4 Mechanical

The earthquake design loads increase as the height above ground level increases. The load factor for this increase in height varies from 1 at ground level to 2 at the top of the structure. Therefore during planning, the requirements for resistance against earthquakes is minimised by locating equipment at ground level. Location of equipment relative to other services and the consequences of failure must be considered.

For example, water storage tanks in high rise buildings are not designed to resist surge loads imposed on the side walls of the tanks by the movement of water during an earthquake. The possibility of rupture of the tank is high. The forces from the earthquake induces imbalance loads from one side of the tank to the other. This can then cause a number of failures depending on the type of structure including:

- tearing of welds between walls and base plates;

- shifting of the tank on its support (sliding) having insufficient lateral resistance;

- cracking of concrete and/or masonry walls;

- buckling of the walls; and

- spillage due to insufficient freeboard.

Electrical transformers, switch rooms, and lift motor rooms are often located in floors below water tanks. Rupture of the tank can then cause shorting of electrical equipment causing failure of mains electricity supply and backup power generation.

Fuel supply lines to diesel or gas-fired backup generators can shear due to differential movement. Similarly, the shearing off of vibration isolation brackets allows equipment to move, thus heightening the likelihood of supply lines being broken.

1.5 Electrical

As indicated in Section "1.4 Mechanical", service components are subject to increased load factors as their respective location within a building increases in height. This is also true for electrical components. Hence, to minimise the stability requirements for electrical equipment they should be located in the lower sections of the building. This also assists in the maintenance of the equipment both on a (generally) daily basis and also after an emergency such as an earthquake.

Electrical components should be located away from, or protected from liquid conduits such as pipelines and drums which can burst, buckle and spill during an earthquake. If the electrical circuit shorts, the successful operation of backup systems can also be jeopardised.

Differential movements between fixed and moving items can cause wires to be pulled from fittings. It is therefore important that:-

- Sufficient loose wire is provided between static and moveable items and that all wiring is adequately anchored; and

- Electrical equipment is adequately anchored to the floor to prevent breaking free.

Items that are located on shelves, if not secured properly, can slide off or the shelf can collapse due to the imposed load. It is common during earthquakes for bottles, books etc. placed on shelves to slide off the end of shelves many metres away. Emergency supply battery packs are no different when stacked on shelves and these need to be supported both horizontally and vertically for constraint purposes.

1.6 Architectural

In the planning stages, consideration needs to be given to all vulnerable elements and whether such elements can be eliminated, reduced, or controlled.

The following items illustrate the type of things that need to be considered in order to enhance the performance of a building during an earthquake:

- there are no soft storeys;

- the building is not an irregular shape:

- tall slender objects are securely fixed in place (top and bottom);

- items cannot slide off shelves or support structures;

- stiff building elements are positioned symmetrically throughout the building (e.g. lift shafts and stair wells or masonry shear walls);

- masonry walls may have to be reinforced to suit the design requirements of AS1170 Part 4;

- ceilings and light fittings are fixed in place both horizontally and vertically;

- the building is located to minimise earthquake design loads with respect to locality, soil profile and post-disaster function requirements;

- post-disaster function buildings are located away from high risk areas;

- in earthquake situations, building occupants must exit a building as quickly as possible ie. within minutes (not tens of minutes) - Are there sufficient exit doors (size and number) to cater for the egress of occupants, etc?;

- when the building moves will the door jam shut preventing occupants from exiting;

- fires often start after earthquakes - Will the sprinkler system be operable after the earthquake?

- if an earthquake occurs can the building site be accessed by emergency vehicles?;

- can external communications be made (telephone, radio) - where are they located?;

- can external facilities such as road network, water supply, power, communications and sewerage still be provided?;

- can the accessibility of sections within the building, from outside, be improved so as to facilitate emergency rescue access?

1.7 Hydraulic

In the design of hydraulic services, allowances for movement between in-ground and above-ground fixtures should be made. Ensure that pipes are located away from electrical installations which may short-circuit if pipes rupture. Ensure pipes are fixed laterally and vertically in position. If pipes are free to move, movement joints must be provided.

1.8 External Constraints

Consider the capability of existing services, such as water, power, sewerage and communication and the impact of their failure on the building. Will their capacities be adequate for the building's requirements should an earthquake occur? Do existing services need to be upgraded to meet the expected requirements? If the provision or upgrading of external facilities is not feasible, what emergency contingencies are in place to overcome any shortfalls in capacity should there be a failure.

1.9 Emergency Services

Emergency services such as Police, Fire, Ambulance, Rescue Teams, Security, Local Authorities and other Government Agencies should be consulted to ensure that their needs are considered:

- Road access

- Communications

- Power

- Egress

- Access

Has a list of equipment been made for use in disaster strategies? Ensure that records of the various Emergency Service providers in the building's area have up to date information on the building and its occupants. Updates should be undertaken at intervals not exceeding six (6) months.

Design

- DESIGN OF NEW BUILDINGS

2.1 Soil Conditions

The soil encountered at a site can significantly increase the imposed earthquake loads on a building and its elements. The type of foundation used e.g. piled, piers, pad, strip or raft footings should reflect the local conditions.

Furthermore, the potential for subsequent modification of ground conditions must be considered, e.g. liquefaction of loose sands may occur on skin friction piles rendering this type of pile inappropriate.

2.2 Building Classification

The classification of the building directly alters the factors used to determine the loads applied to the structure for design against structural failure due to earthquakes. Ensure that the design load factors that are used are applicable for the specific use of the building and for post-disaster functions if required and also to suit any future changes to the building's use, if it is known at the design stages.

2.3 Structural

Minimum design and detail requirements apply to various types of structures according to their use and classification, locality and soil types.

Minimum design and structural framing requirements for various types of buildings are identified in AS1170 Part 4. For example:

| Structure Type | Typical Building Description | Design Level |
| --- | --- | --- |
| III | Hospitals | C |
| II | Assembly Hall | B |
| I | Not Residential and neither II or III | A |
|  | Residential | H1 |

Consideration of the transfer of loads is important when designing for resistance and distribution of earthquake induced loads. Analysis of load distribution would typically include:

- where the building is of irregular shape, ensure that the varying vibration modes for the different sections of the building are uniform;

- ensure that the vertical component of any imposed earthquake load is considered in the design, especially where columns support flat plate slabs;

- ensure that retaining walls that act as support for upper floors are integrally connected to foundations and columns so as to prevent differential movement between floors and columns;

- ensure that reinforcement from retaining walls continues through the non-retaining section of the walls into the floors above; This ensures loss of support for upper floors does not occur due to lateral movement and rotation of the wall underneath;

- consider the effect of the differential movement and application of load, as the earthquake wave passes through a building;

- are masonry walls in accordance with the detail and design requirements of AS1170 Part 4?

- ensure that gable end walls are adequately supported and tied to fixed members;

- ensure sufficient bonding to brick ties is achieved;

- ensure sufficient strength is obtained to support any "soft floor" systems;

- ensure even distribution of all forces and stresses throughout the building, i.e. locate stair shafts and lift wells symmetrically;

- ensure openings around windows are adequately reinforced.

- ensure extensions to existing buildings are physically attached to prevent differential movement.

- ensure masonry screen walls do not exceed stability limits for overturning due to horizontal earthquake loads.

Refer also to:

- Design of New Buildings

2.4 Mechanical

Earthquake-induced load on mechanical equipment increases with height. Locating equipment at the top of a building effectively doubles the applied load.

Both good structural design and specifically located vibration isolators must be provided to resist these applied loads. Rigid fixings should also be designed to resist horizontal and vertical loads - friction forces are generally lost when the building vibrates.

Pipework attached to equipment should have provision for differential movement between the structure and the equipment. Vibration of equipment will occur in all directions.

Joints in pipework should be able to accommodate the expected rotations and lateral movements. Fixing of pipework at structural isolation joints should be spaced sufficiently apart to allow lateral movement between sections in all directions.

2.5 Electrical

Refer also to 2.4 Mechanical as similar comments for mechanical equipment also apply to electrical equipment. In addition:

- ensure adequate fixings to critical items are provided to allow continued operation;

- ensure wiring is adequately fixed so that it does not pull from sockets and connections during an earthquake;

- ensure loose items have restricted movement and sufficient loose wire is provided to allow for the necessary movement;

- ensure items are located away from pipelines and other liquid carrying conduits that may burst during an earthquake;

- if power is discontinued ensure that items that are required for building operations can be manually operated eg; electrically operated doors; and

- ensure that equipment is restrained both laterally and vertically.

Applied forces on equipment increases as the location in the building increases in height. The applied factor varies from 1 at ground level to 2 at the top of the building ie. applied loads are doubled.

2.6 Architectural

During the design of a building to minimise earthquake damage the following aspects should be considered;

- are the selected building materials suitable to minimise damage from an earthquake?

- gable and parapet brick walls are renowned for failure during earthquakes, can these be eliminated?

- are there sufficient egress points to enable mass exit in the event of disaster? Are the access to these exits also capable of carrying the population numbers for which the building is designed?

- are tall cupboards and support structures adequately fixed to walls?

- are heavy objects located at the lowest part and centrally in the building?

- can soft storeys be eliminated?

- can the building be designed as a regular shape?

- are suspended ceiling grids adequately restrained?

- are the tops of partition walls adequately restrained?(fixing to suspended ceiling grid may not be sufficient).

- are masonry walls designed to meet the detail and design requirements of AS1170 Part 4?

- are brick ties adequately corrosion protected from industrial and environmental attack (most brick ties in Newcastle were severely corroded due to industrial elements)?

2.7 Hydraulic

Refer also to 2.4 Mechanical as hydraulic services provisions are similar. The following are typical of the items that need to be considered for earthquake damage mitigation:-

- ensure pipes are rigidly fixed in position at the ends, with flexible couplings being provided to allow for movement;

- can support brackets provide restraint both vertically and horizontally?;

- if vibration isolation supports are provided, ensure joints can provide the necessary movement under earthquake conditions;

- ensure expansion longitudinal, lateral and vertical movement joints are provided between independent rigid systems;

- valves and junctions which are generally much heavier than standard pipe lengths require support. If the valve is supported by the adjacent pipework, can the pipework and flanges carry the applied shear load due to the mass of the valve, under earthquake loading? If not, provide an adequate fixing.

2.8 External Constraints

Refer to External Site Considerations

2.9 Emergency Services

Refer to Emergency Services

Asset Management

Refer also to:

- Assessment of Existing Buildings

- Checklist - Asset Management

3.1 Soil Conditions

During the life of a building, measures should be taken to ensure that conditions of the underlying soil remain unchanged, or are improved. This is necessary to ensure that imposed earthquake loads do not increase, and that the capacity of the soil to carry the load is not reduced. (eg. water table level change, saturated clays, etc.).

Planting of suitable trees and shrubs can ensure that the water table remains constant or is reduced; it also helps in maintaining the properties of the soil. Care must be taken the plants are not over watered - detrimental to the properties of the soil - and that the plants' root systems do not cause failure of the building's foundations.

The strategic management plan that is developed should include provision for the maintenance of the surrounding ground to ensure that the soil profile and soil properties are not altered from that existing prior to the construction of the building. This is particularly important when constructing in loose sands and silts, where liquefaction can occur, potentially causing differential settlement of the building. It is equally important in other types of soil materials where the strength of the material is reduced, as this can cause slippage of embankments due to ground vibration.

3.2 Building Classification

During the life of a building, changes in use can lead to a change in classification. Such a change in classification of part or all of the building may inflict a penalty on the asset management plan by increasing the design loads which the building must be able to resist in the case of an earthquake.

Asset managers should ensure the strategic plan developed for the building includes the use of the building and its requirement for post-disaster functions (if required). If the building is designed for a domestic classification then it will not be able to upgrade to a higher (commercial, institutional) classification and still satisfy earthquake load resistance requirements. Property managers and designers should ensure that when a building changes classification or use, the building is able to meet the requirements of AS1170 Part 4 and the Building Code of Australia requirements.

3.3 Structural

Ensure that any changes made to the building do not reduce the capacity of the existing structural system.

Consider:

- installation of masonry walls can stiffen one section of the building and induce higher loads in other parts of the building;

- removal of some sections of the structure may alter the distribution of load and hence alter the stability under earthquake conditions;

- adjacent buildings which are built close to each other should have similar relative stiffness and periods of vibration, otherwise excessive damage may be caused by the two buildings colliding with each other;

- minimum space between independent buildings should be 50mm times the number of floors in the shorter building, otherwise they should be continuously attached and have similar stiffness.

3.4 Mechanical

Equipment may be required for post-disaster functions and so must be maintained in good working order to ensure it's function in an emergency situation.

- Any new equipment installed should be designed and fixed to meet the same "in-service" criteria as the original equipment (assuming the original equipment has been installed correctly);

- ensure securing bolts are in good condition - if not, repair;

- check that vibration support systems can support the applied earthquake loads;

- check that pipe support brackets can provide resistance to both horizontal and vertical loads;

- ensure any differential movement between pipe support and equipment can be accommodated by the pipework, if not, provide a flexible joint.

3.5 Electrical

- where fixings have been provided, ensure they are correctly installed;

- ensure sufficient loose wiring is provided so as to allow movement between more rigid connections;

- ensure any loose item's movement is restricted;

- ensure any new equipment fitted, meets the same suitability and functional requirements as that of the existing building equipment;

- ensure any repairs are fully completed and all anchor bolts are correctly installed;

- ensure sufficient space is provided between individual items so as to prevent damage when vibration occurs;

- ensure wiring is securely fixed to connections.

3.6 Architectural

- if the building classification is changed, will it increase earthquake design load requirements?

- if the building design has altered, is the new work consistent and integral with the old work?

- is the building still operating in the manner for which it was originally designed?

- is a Disaster Strategy in place?

- are all security personnel aware of the Disaster Strategy?

3.7 Hydraulic

- ensure all equipment is included in the strategic plan.

3.8 External Constraints

- computer equipment should be secured in a fashion that prevents sliding off desks or other supports.

3.9 Emergency Services

- ensure modification to the building meets with emergency services' requirements.

Refer to Emergency Services

Maintenance

Refer also to:

Checklist - Maintenance of existing buildings

4.3 Structural

- ensure that the structure is in good condition e.g. ensure corrosion of all metal components is eliminated, brick-ties have no degradation, cracks in masonry are repaired, check for foundation settlement, and all bolts are fixed into the appropriate connections.

- Performance of all structural members must be maintained as originally designed.

4.4 Mechanical

- ensure that all equipment is correctly and adequately fixed in place e.g. generators, air conditioning ducts, pipework,water tanks, etc.

4.5 Electrical

- ensure emergency lighting systems are checked and repaired regularly,

- ensure all equipment is adequately anchored; and

- ensure all wiring is adequately fixed into connections.

4.6 Architectural

Ensure that all:-

- window sealants are flexible;

- ceiling tiles are fixed (i.e. replace clips);

- access and egress passageways are clear;

- light fittings and alike are adequately fixed;

- tall cupboards supported at top and will not slide or fall over;

- pipework is adequately fixed in place; and

- expansion and contraction joints are upgraded (correctly) and they are not seized.

4.7 Hydraulic

Ensure pipework integrity is maintained i.e.:

- cracks and supports are repaired;

- insulation is checked and maintained.

4.9 Emergency Services

- ensure access and egress for emergency personnel and vehicles is maintained.

- ensure safety equipment is maintained including.:

  - fire fighting equipment;

  - fire escape doors, etc.

Post-Disaster and Disposal

Refer also to:

- Post-disaster and disposal

5.1 Soil Conditions

After an earthquake, the soil may become fractured or loose, considerably altering its capacity to support load.

Aftershocks also pose a significant threat. Although not as powerful as the original quake, structures and foundations will likely be more vulnerable (having already sustained some damage).

An influx of water (perhaps from broken mains) could significantly alter the bearing capacity of the local soil. The post disaster Emergency Plan should anticipate this as a potential problem.

5.2 Building Classification

Refer to:

- Post-disaster and disposal

5.3 Structural

In the event of an earthquake, the following checks must be carried out:

- determine extent of damage;

- determine if structure can be repaired or requires demolition (heritage issues may need to be addressed);

- if the structure is pre or post tensioned, determine the safe work practices which will enable rectification and/or demolition.

Refer also to:

- Post-disaster and disposal

5.4 Mechanical

In the event of an earthquake, the following checks must be carried out:

- if equipment has come away from its support, ensure that it is stable before attempting any rectification as aftershocks are likely and injury to rescue workers may occur;

- is key equipment still suitable for use? If not, ensure repair

- is further damage likely to occur due to aftershocks? Seek advice from Emergency Services Personnel.

Refer also to:

- Post-disaster and disposal

5.5 Electrical

In the event of an earthquake, the following checks must be carried out:

- check capacity of equipment for reuse;

- if equipment is to be replaced, ensure power is disconnected;

- if property is severely damaged, ensure power is disconnected and live wires are not present if mains power is returned.

Refer also to:

- Post-disaster and disposal

5.6 Architectural

In the event of an earthquake, the following checks must be carried out:

- assess damage;

- is the building suitable for continual use? - conduct 'needs' inspection

- is the building repairable? - conduct 'needs' inspection

- should the building be demolished?

- are there any heritage issues?

- if the building is repaired, such repair must meet at least the current building codes.

- if any repairs are carried out, can the activities of the building be maintained while installing new support structures, effecting repairs?

Refer also to:

- Post-disaster and disposal

5.7 Hydraulic

In the event of an earthquake, the following checks must be carried out:

- ensure pipework is not cracked;

- replace damaged pipework;

- is the existing system adequate? - if not, provide recommendations to improve;

- test for possible leakages including smoke and pressure tests.

Refer also to:

- Post-disaster and disposal

5.8 External Constraints

Rectification of external services will take time; some temporary services may become almost semi-permanent. Management Plans should reflect this likely outcome.

5.9 Emergency Services

Refer to Emergency Services

Risk

If the building has been designed in accordance with the appropriate codes and building requirements for earthquake mitigation, then the risk of failure due to an earthquake should be minimal. However, if there are components in the building that fail, or cause the building not to operate in the required manner e.g. loss of power, then the risk of failure is increased.

Refer also to Assessment of Vulnerability

6.1 Soil Conditions

Soil conditions are a major risk component in earthquake design mitigation. The soil type and building foundation design are major factors in determining the applied design loads and the ability of the structure to resist those applied loads. Detailed assessment is crucial.

6.2 Building Classification

The building classification defines the use of a building. In turn, this defines some of the requirements on types of construction, limits on building sizes, fire compartments and occupancy levels for the purposes of fire resistance and alike. It does not define the type of construction required for earthquake resistance. Hence, the building classification alone cannot be used to attribute a level of vulnerability.

It could be assumed therefore, that if the occupancy level is low then the building would also have a low risk of failure, but this is not the case. In fact, it is the type of construction used in the "low risk" buildings that puts the occupants and the building in a high vulnerability category. For example, a 2 storey "six-pack" of domestic units which has a reasonably low level of occupancy, little post-disaster functionality, basement car park with masonry load bearing walls for support with little or no continuity from foundation level to roof has a very high risk (or is extremely vulnerable to failure) in the event of an earthquake.

Similarly, for example, a Class 10 building/structure (to BCA classification) which covers mast, flagpoles and antennas, can be attributed different levels of risk. A flagpole may have a minor post-disaster function, whereas an antenna which is critical for radio communications between police, the public and emergency services, would probably have a high post-disaster function. Consideration of this must always be taken into account when assessing risk.

Those buildings which have the potential to contain a large number of people during an earthquake, or have a post-disaster function, have the highest potential risk associated with them, but must be designed to have the lowest potential risk.

The following typical risk levels have been determined by the number of people that could be injured or critically injured due to an earthquake in the event of failure.

| Class | Description | Risk |
| --- | --- | --- |
| 1 | Residential: single dwelling or townhouse | Low * |
| 2 | Residential: sole occupancy | Low * |
| 3 | Residential: boarding house, hotel, aged care etc. | Low * / Medium |
| 4 | Residential: a dwelling attached to a Class 5, 6, 7, 8 or 9 building | Low * / Medium |
| 5 | Offices | Medium |
| 6 | Retail (Shops) | Medium |
| 7 | Car Park, Wholesale store | Low |
| 8 | Processing Plant | Medium |
| 9 | Health / Assembly | High / Medium |
| 10 | Masts / Antenna | Low / High |

* These classes of buildings may have a low risk associated with them in terms of post-disaster functions but may be extremely vulnerable due to the general type of construction (unreinforced masonry).

6.3 Structural

Refer to:

- Risk

- Aspect Identification

6.4 Mechanical

Refer to:

- Risk

- Aspect Identification

6.5 Electrical

Refer to:

- Risk

- Aspect Identification

6.6 Architectural

Refer to:

- Risk

- Aspect Identification

6.7 Hydraulic

Refer to:

- Risk

- Aspect Identification

6.8 External Constraints

Refer to:

- Risk

- Aspect Identification

6.9 Emergency Services

Refer to:

- Risk

- Aspect Identification

Built Environment Research Unit, Building Division, Qld Department of Public Works